## Start Here
General Guidelines:
1. Be slow, systematic, and precise in testing. If there is not a clear understanding of the system to be tested and expected results, then clarify before testing to avoid damage!
2. Never erase old data, it can be useful for troubleshooting. If you failed a set of tests, put a copy of the test procedure below that one, and repeat the tests!
3. There is example data in these forms. Once you understand what you want to do, replace the example data with your project data.
4. Save your workbook with the Team number and short name (e.g. "15 robot arm")
Instructions:
1 | Complete the glossary below
2 | Insert your system requirements on the "Requirements" tab.
3 | Consider what testing you need to do, and complete the "Type of Test" column for all requirements.
4 | Complete documentation of at least 4 tests: 3 from (UTS, UTM) and one integration test. Copy and modify sheets as necessary
5 | Present an overview of your 4 tests as a PowerPoint presentation on the assigned date. Submit this Excel Workbook for grading.
6 | Complete the actual tests! Record your results and comments. You will pull some of this data to your reports.
7 | Prepare your Testing Report and submit
Glossary
term | definition:
White Box | A system or component, the inner workings of which are known
Black Box | A system or component, which produces outputs from inputs, using unknown methods
Unit Test | A test of a single subsystem or function
Matrix Test | A test that checks a system's response to a range of values for a single input, such as a varying an analog input across its expected range
Step-by-Step Test | A test that checks a system's response to a specific sequence of inputs
test coverage | The percentage of requirements that are tested by a testing scheme
integration testing | A test of multiple subsystems or the entire project system
Acceptance test | A test conducted by or under the direct supervision of the project owner/customer to demonstrate to the owner that the project meets requirements
UUT | Unit Under Test; the device being tested
Note on A18: ====== ID#AAAAWblTbyc Robert Severinghaus (2022-03-03 02:33:18) see DECE Ch. 7

## Greenhouse Requirements
TEACHING GREENHOUSE - MASTER TESTING LIST - UPDATED 1 APRIL 2022
Type of Test | Status | Req # | Requirement | Remarks
Inspect |  | 1.1.1 | The north house shall be equipped with at least two temperature and humidity sensor modules. | The sensors exist and have been functionally tested, but have not yet been delivered to the customer.
Inspect |  | 1.1.2 | The south house shall be equipped with at least eight temperature and humidity sensor modules.
UTM |  | 1.1.3 | Temperature sensors shall be accurate to +/- 2℉ or better.
UTM |  | 1.1.4 | Humidity sensors shall be accurate to +/- 5% or better.
UTS |  | 1.1.5 | All sensors shall operate properly in temperatures from 40 to 120 ℉. | Tests were passed but the tests did not cover the entire specified ranges.
UTS |  | 1.1.6 | All sensors shall operate properly from 0 to 100% humidity.
Inspect |  | 1.2.1 | The greenhouse shall have at least 3 mobile sensors that are available to monitor the moisture content of the soil in any container.
UTM |  | 1.2.2 | Soil moisture content readings shall be accurate to +/- 5% or better.
UTS |  | 1.2.3 | Soil moisture sensors shall comply with the operating conditions specified for temperature and humidity sensors.
UTS | * | 2.1.1 | Temperature and humidity data shall be retrieved from sensors and stored at intervals of 15 minutes or less.
UTS |  | 2.1.2 | Environmental logs shall include, at a minimum, the temperature and humidity reported by each sensor and the time and date of the reading.
Inspect |  | 2.1.3 | The system shall have adequate storage to retain logged data for at least two years.
Integrate | * | 3.1.1 | A web interface shall numerically show temperatures and humidities from the latest reading.
UTS |  | 3.1.2 | The web interface shall be accessible from off campus without use of the VPN.
Inspect |  | 3.2.1 | The web interface shall be able to show graphs of recent temperature and humidity data, either individually per sensor, or using an average for each section of the greenhouse.
UTS |  | 3.2.2 | The time range of the graphs shall be user-selectable (allow the user to view data from the last 24 hours, 7 days, month, etc). | Client prefers all such graphs shown simultaneously.
UTS |  | 3.2.3 | The system shall provide a method for users to retrieve a CSV file containing all logged data, without requiring user knowledge of linux tools such as scp or sftp.
UTS & Integrate | * | 4.1.1 | A smartphone alert will notify Tina Ayers or other greenhouse personnel when user-defined safe temperature or humidity ranges are exceeded.
UTS |  | 4.1.2 | A method shall be provided for users to add/remove alert recipients.
UTS |  | 4.1.3 | A method shall be provided to adjust temperature setpoints and any control conditions.
(not testable) |  | 4.1.4 | The alert will be in a concise, numerical listing of data. | Ambiguous
UTS |  | 4.1.5 | The system will notify all alert recipients within 5 minutes of an unsafe condition being detected.
UTS |  | 4.2.1 | All alert recipients will be notified within five minutes of a sensor failure being detected.
Inspect |  | 4.2.2 | At least two extra sensor modules will be left behind to allow for user replacement of failed modules.
Inspect |  | 4.2.3 | Documentation will be provided so that new modules can be constructed if necessary. | Documentation to be produced in the coming weeks
Inspect |  | 5.1.1 | At least two mixing fans shall be installed in the south house. | Fans on hand but not installed
Inspect |  | 5.1.2 | Mixing fans shall be rated for wet locations.
Inspect |  | 5.1.3 | Mixing house fans shall not be battery-powered.
UTS |  | 5.1.4 | The system shall be able to turn the fans on and off. At minimum, the following control modes will be provided:
UTS |  | 5.1.4.1 | Always on
UTS |  | 5.1.4.2 | Always off
UTS |  | 5.1.4.3 | On during user-specified hours
UTS & Integrate |  | 5.1.4.4 | On when excessive temperature differentials are detected within the greenhouse.
Integrate |  | 5.2.1.1 | The system shall control the south house glycol heater to maintain a user-selected temperature in the south house. | Client no longer needs this functionality.
Inspect |  | 5.2.1.2 | The temperature selection method shall be calibrated in degrees Fahrenheit.
Integrate |  | 5.2.2.1 | The system shall control the wet wall and south house exhaust fan to maintain a user-selected temperature in the south house.
Inspect |  | 5.2.2.2 | The temperature selection method shall be calibrated in degrees Fahrenheit.
Inspect |  | 6.1.1 | Equipment left in the greenhouse at the conclusion of the project shall not use solderless breadboards or other temporary circuit construction techniques.
Inspect |  | 6.2.1 | All equipment shall adhere to relevant safety standards. | We are not qualified to test this.
Inspect |  | 6.2.2 | Equipment operating above 12V shall comply with the National Electrical Code.
Note on A3: ====== ID#AAAAWblTbyk Robert Severinghaus (2022-03-03 02:33:18) How will you test this requirement? Inspect = inspection (e.g. "system will have 2 buttons", "system will be red in color" "PCB will be less than 2 inch x 2 inch", you can do this by visual inspection) UTM = Unit Test Matrix UTS = Unit Test step-by-step Integrate = Integration test
Note on B3: ====== ID#AAAAWblTbyU Robert Severinghaus (2022-03-03 02:33:18) These are best as color-coded. Update these throughout your testing. Black = not testable empty = not tested yet green = test passed yellow = test partially passed red = test failed * = very important requirement (maybe <5 of these per system, helps you prioritize)
Note on D3: ====== ID#AAAAWblTby4 Robert Severinghaus (2022-03-03 02:33:18) Copy in either your requirements from EE 476C or your most recent set of revised requirements. Update them if you or your client has changed the requirements. It is best to strikethrough the old requirement and insert the new. This shows it is intentional and not just an omission.

## System images
SYSTEM ARCHITECTURE
AIR SENSOR SCHEMATIC

## Test 1 Temperature Accuracy
Test number | 1
Requirement Tested: | 1.1.3 | Temperature sensors shall be accurate to +/- 2℉ or better.
Test Case name: | Temperature Accuracy
Type | White Box
Hardware version: | 1 | Tester: Ruopeng |  | Date: | 2022-03-16
Setup instructions: | We need an air-conditioned room with automatic temperature regulation. A standard thermometer and sensor module are required. Set the air conditioner to the lowest temperature in the adjustable range and keep it for a period of time. After ensuring that the indoor temperature remains stable, set the air conditioning temperature to the maximum. Observe and record the standard thermometer reading and sensor transmission reading at the same time. Set 10 standard thermometer readings between 70 and 90 ° F. the readings should not differ by more than 2 degrees Fahrenheit throughout the process.
Results
Test | Input | Expected Result | Pass | Fail | N/A | Comments
1 | Room Temperature = ~70°F | Reading Difference should be less than 2°F | √
2 | Set room temperature = ~90°F | No result
3 | Wait for the readings | No result
4 | Standard Temperature = 72°F | Reading Difference should be less than 2°F | √
5 | Standard Temperature = 74°F | Reading Difference should be less than 2°F | √
6 | Standard Temperature = 76°F | Reading Difference should be less than 2°F | √
7 | Standard Temperature = 78°F | Reading Difference should be less than 2°F | √
8 | Standard Temperature = 80°F | Reading Difference should be less than 2°F | √
9 | Standard Temperature = 82°F | Reading Difference should be less than 2°F | √
10 | Standard Temperature = 84°F | Reading Difference should be less than 2°F | √
11 | Standard Temperature = 86°F | Reading Difference should be less than 2°F | √
12 | Standard Temperature = 88°F | Reading Difference should be less than 2°F | √
13 | Standard Temperature = 90°F | Reading Difference should be less than 2°F | √
Note on B5: ====== ID#AAAAWblTbyw Robert Severinghaus (2022-03-03 02:33:18) white box or black box

## Test 2 Humidity Accuracy
Test number | 2
Requirement Tested: | 1.1.4 | Humidity sensors shall be accurate to +/- 5% or better.
Test Case name: | Humidity accuracy test
Type | White Box
Hardware version: | 1 | Tester: Jiaxin Liu |  | Date: 03/25/2022
Setup instructions: | We need an airtight room with a humidifier to regulate humidity. A standard Hygrometer and the humidity sensor module are required. Test initial humidity in a room with 20% humidity. Then, open the humidifier to adjust the room humidity more than 60%. Set 9 readings between 20% and 60%. Reads the sensor value every 5% interval from watching the hygrometer. The expected result of reading difference should be less than 5%
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1 | Room Humidity= 20% | Reading Difference should be less than 5% | √
2 | Room Humidity= 25% | Reading Difference should be less than 5% | √
3 | Room Humidity= 30% | Reading Difference should be less than 5% | √
4 | Room Humidity= 35% | Reading Difference should be less than 5% | √
5 | Room Humidity= 40% | Reading Difference should be less than 5% | √
6 | Room Humidity= 45% | Reading Difference should be less than 5% | √
7 | Room Humidity= 50% | Reading Difference should be less than 5% | √
8 | Room Humidity= 55% | Reading Difference should be less than 5% | √
9 | Room Humidity= 60% | Reading Difference should be less than 5% | √

## Test 3 Sensor Data Rate
Test number | 3
Requirement Tested: | 2.1.1 | Temperature and humidity data shall be retrieved from sensors and stored at intervals of 15 minutes or less.
Test Case name: | Sensor Data Rate
Type | White Box
Hardware version: | 1 | Tester: Emilia Connelly |  | Date: | 2022-04-01
Setup instructions: | Set up at least 5 air sensors. After placing sensors, verify that all the sensors are communicating to the server. On the console, set all sensors as deployed in the South House.
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1 | Record starting time of test. |  |  |  | n/a
2 | Allow sensors to run for three hours. |  |  |  | n/a
3 | After the three hour interval, inspect the logs |  |  |  | n/a
4 | Inspect logged data in the database | The data should conform to the 2.1.1 Requirement.
5
6
7
8
9
10

## Test 4 Live Alerting Test
Test number | 4
Requirements Tested: | 4.1.1 | A smartphone alert will notify Tina Ayers or other greenhouse personnel when user-defined safe temperature or humidity ranges are exceeded.
| 4.1.3 | A method shall be provided to adjust temperature setpoints and any control conditions.
| 4.1.5 | The system will notify all alert recipients within 5 minutes of an unsafe condition being detected.
Test Case name: | Live Alert integration test
Type | White Box
Hardware version: | 1 | Tester: Emilia Connelly |  | Date: | 2022-04-01
Setup instructions: | Required: access to a refrigerator in the testing area; stopwatch. Using the Alarm Recipients tab in ControlDesk, set ONE testing observer to receive smartphone alerts. Using the Sensor Configuration tab in ControlDesk, set all air sensors to INACTIVE, except set one air sensor to SOUTH (the "active sensor"). Power up the active sensor in the testing area and verify that temperature data is received and displayed in ControlDesk. Allow the reported temperature to stabilize.
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1 | Initial conditions | No alert
2 | Place an active air sensor in refrigerator; observe data readout on ControlDesk application | n/a
3 | When the active sensor first reports a temperature under the set Low Temperature threshold, start the stopwatch | n/a
4 | Stop the stopwatch after 5 minutes or when the testing observer's phone receives a text alert from the greenhouse system | Cold alert within 5 minutes
5 | Remove the sensor from the refrigerator; observe the reported temperature | n/a
6 | When the active sensor first reports a temperature above the set Low Temperature threshold, restart the stopwatch | n/a
7 | Stop the stopwatch after 5 minutes or when the testing observer's phone receives a text alert from the greenhouse system | All-clear message within 5 minutes
8 | In the ControlDesk Alarm Recipients tab, add another testing observer to receive alerts | n/a
9 | Place active sensor in refrigerator; observe data readout on ControlDesk application | n/a
10 | When the active sensor first reports a temperature under the set Low Temperature threshold, start the stopwatch | n/a
11 | Stop the stopwatch after 5 minutes or when the testing observer's phone receives a text alert from the greenhouse system | Cold alert within 5 minutes to all testers
12 | Remove the sensor from the refrigerator; observe the reported temperature | n/a
13 | When the active sensor first reports a temperature above the set Low Temperature threshold, restart the stopwatch | n/a
14 | Stop the stopwatch after 5 minutes or when the testing observer's phone receives a text alert from the greenhouse system | All-clear message within 5 minutes to all testers

## Example Unit Test, Step-by-Step
Test number | 2
Requirement Tested: | 1.5.2.1 | All sensors shall operate properly in temperatures from 40 to 120 ℉.
Test Case name: | Voltage fault detection
Type
Hardware version: |  | Tester: |  | Date:
Setup instructions: | The UUT will have 4 voltage sources to sense. Three of the voltage sources can be a 1.5 volt battery. The fourth voltage source is a power supply with adjustable voltage. Measure the battery voltage. Set the voltage source to the same voltage. Connect 3 wires from battery to inputs 1,2,3.
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1 | 1,2,3=battery, 4 = ground | voltage fault detected
2 | reset system. 1,2,3=battery, 4=power supply | no fault detected
3 | 1,2,3= battery, slowly lower power supply voltage | fault detect at (battery voltage - 0.1 Volts) = __________V
4 | reset system. 1,2,3=battery, 4=power supply | no fault detected
5 | 1,2,3= battery, slowly raise power supply voltage | fault detect at (battery voltage + 0.1 Volts) = _________V
6
7
8
9
10
Note on B3: ====== ID#AAAAWblTbyg Robert Severinghaus (2022-03-03 02:33:18) An exact copy from your requirements list.
Note on B6: ====== ID#AAAAWblTby0 Robert Severinghaus (2022-03-03 02:33:18) white box or black box

## Copy of Example Unit Test, Step
Test number
Requirement Tested: | 4.1.1 | A smartphone alert will notify Tina Ayers or other greenhouse personnel when user-defined safe temperature or humidity ranges are exceeded.
Test Case name: | Unsafe Condition Alerting: Unit Test
Type | UTS
Hardware version: |  | Tester: |  | Date:
Setup instructions: | Log in to the console as console@tghpi. If the ControlDesk application does not automatically start, start the ControlDesk software manually. Disconnect the Raspberry Pi from the Getting Green wireless network; this will prevent any data reports from live sensors from interfering with the test. In the Alarm Recipients tab of the ControlDesk, verify that the tester is set to receive alerts for unsafe conditions. Create a new sensor definition for the test:
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1
2
3
4
5
6
7
8
9
10

## Example Integration Test
Test number | 3
Requirements Tested: | 1.1.1 | Presets must be predetermined for the LiPo battery being charged, this will automatically set the voltage and current inputs to the LiPo battery charger to reduce overall user input error
| 1.4.1 | Ensures all battery cells are equally charged and balanced during charging
| 1.5 | User settable alarms limits via physical buttons and/or bluetooth for fault conditions detection for defective cells within the battery pack
Test Case name: | User integration testing
Type
Hardware version: |  | Tester: |  | Date:
Setup instructions: | Tester starts with battery disconnected. Turns on charger unit. Record cell voltages of battery. 1 ______ V 2 _____ V 3_____ V 4_____ V Plug in battery to be recharged.
Results
Step | Action | Expected Result | Pass | Fail | N/A | Comments
1 | (Unit detects battery type) | LCD display shows correct battery type (1,2,3, or 4 cell LiPo)
2 | user selects charge using buttons and selects start | LCD shows charging amperage and time remaining
3 | user select alarm limits, time of 1 min. | After 1 minute, Alarm displays on LCD and audio tone for 1 minute alarm.
4 | after 2 minutes, disconnect battery and test the voltage of all cells | All voltages nearly equal (+/- 0.4V) : 1 ______ V 2 _____ V 3_____ V 4_____ V
5 | connect battery again to charger, user select charge, and wait until charging is complete. Measure voltage of all cells | All voltages equal (+/-0.1 V): 1 ______ V 2 _____ V 3_____ V 4_____ V
6
7
8
9
10
Note on B9: ====== ID#AAAAWblTbyY Robert Severinghaus (2022-03-03 02:33:18) white box or black box